## Modbus_var
Address |  | Reg. N° | Parameter | Description | Display Mode | Type | Unit | Value |  |  | Comment | Abbreviations for Type
hexadecimal | decimal | [6 empty] | Min. | Max. | Default
0x0001 | 1 | 1 | ALM_COOLER_FREEZE_F | Water Exchanger Freeze Protection | 1bit BOOL | DI |  | 0 | 1 | 0 |  | CO | COILS_MEDIA
0x0005 | 5 | 1 | ALM_LOW_SUCTION_A_F | Circuit A Low Saturated Suction Temperature | 1bit BOOL | DI |  | 0 | 1 | 0 |  | IR | INPUT_REG_MEDIA
0x0006 | 6 | 1 | ALM_LOW_SUCTION_B_F | Circuit B Low Saturated Suction Temperature | 1bit BOOL | DI |  | 0 | 1 | 0 |  | DI | DISCR_INPUT_MEDIA
0x0008 | 8 | 1 | ALM_HIGH_SH_A_F | Circuit A High Superheat | 1bit BOOL | DI |  | 0 | 1 | 0 |  | HR | HOLDING_REG_MEDIA
0x0009 | 9 | 1 | ALM_HIGH_SH_B_F | Circuit B High Superheat | 1bit BOOL | DI |  | 0 | 1 | 0
0x000B | 11 | 1 | ALM_LOW_SH_A_F | Circuit A Low Superheat | 1bit BOOL | DI |  | 0 | 1 | 0
0x000C | 12 | 1 | ALM_LOW_SH_B_F | Circuit B Low Superheat | 1bit BOOL | DI |  | 0 | 1 | 0
0x000E | 14 | 1 | ALM_COOLER_LOCK_F | Cooler Interlock Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x0010 | 16 | 1 | ALM_CPA1_REVERSE_ROT_F | Compressor A1 Not Started Or Pressure Increase not Established | 1bit BOOL | DI |  | 0 | 1 | 0
0x0011 | 17 | 1 | ALM_CPA2_REVERSE_ROT_F | Compressor A2 Not Started Or Pressure Increase not Established | 1bit BOOL | DI |  | 0 | 1 | 0
0x0012 | 18 | 1 | ALM_CPA3_REVERSE_ROT_F | Compressor A3 Not Started Or Pressure Increase not Established | 1bit BOOL | DI |  | 0 | 1 | 0
0x0014 | 20 | 1 | ALM_CPB1_REVERSE_ROT_F | Compressor B1 Not Started Or Pressure Increase not Established | 1bit BOOL | DI |  | 0 | 1 | 0
0x0015 | 21 | 1 | ALM_CPB2_REVERSE_ROT_F | Compressor B2 Not Started Or Pressure Increase not Established | 1bit BOOL | DI |  | 0 | 1 | 0
0x001C | 28 | 1 | ALM_ELEC_BOX_F | Electrical Box Fault | 1bit BOOL | DI |  | 0 | 1 | 0
0x001D | 29 | 1 | ALM_LOSS_COM_SM_F | Loss of communication with System Manager | 1bit BOOL | DI |  | 0 | 1 | 0
0x001E | 30 | 1 | ALM_LOSS_COM_MS_F | Master/Slave communication Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x001F | 31 | 1 | ALM_NETWORK_EMSTOP_F | Unit is in Network emergency stop | 1bit BOOL | DI |  | 0 | 1 | 0
0x0020 | 32 | 1 | ALM_COOL_PUMP1_F | Cooler Pump 1 Default | 1bit BOOL | DI |  | 0 | 1 | 0
0x0021 | 33 | 1 | ALM_COOL_PUMP2_F | Cooler Pump 2 Default | 1bit BOOL | DI |  | 0 | 1 | 0
0x0025 | 37 | 1 | ALM_REPEATED_HI_DGT_A_F | Circuit A Repeated High Discharge Gas Overrides | 1bit BOOL | DI |  | 0 | 1 | 0
0x0026 | 38 | 1 | ALM_REPEATED_HI_DGT_B_F | Circuit B Repeated High Discharge Gas Overrides | 1bit BOOL | DI |  | 0 | 1 | 0
0x0028 | 40 | 1 | ALM_REPEATED_LO_SST_A_F | Circuit A Repeated Low Suction Temp Overrides | 1bit BOOL | DI |  | 0 | 1 | 0
0x0029 | 41 | 1 | ALM_REPEATED_LO_SST_B_F | Circuit B Repeated Low Suction Temp Overrides | 1bit BOOL | DI |  | 0 | 1 | 0
0x002B | 43 | 1 | ALM_HEAT_LOW_EWT_F | Low Entering Water Temperature In Heating | 1bit BOOL | DI |  | 0 | 1 | 0
0x003F | 63 | 1 | ALM_HP_SWITCH_A_F | Circuit A High pressure switch Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x0040 | 64 | 1 | ALM_HP_SWITCH_B_F | Circuit A2/B High pressure switch Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x0061 | 97 | 1 | ALM_SENSORS_SWAP_F | Water Exchanger Temperature Sensors Swapped | 1bit BOOL | DI |  | 0 | 1 | 0
0x0063 | 99 | 1 | ALM_FLUIDE_FAIL | Possible Refrigerant Leakage Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x0065 | 101 | 1 | ALM_FC_PROCESS_F | Free Cooling Process Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x006D | 109 | 1 | ALM_TANK_EHS_LOW_EFF_F | Tank EHS Low Efficiency Alert | 1bit BOOL | DI |  | 0 | 1 | 0
0x007A | 122 | 1 | ALM_DEMO_SW_PROT_F | Replacement Mode: please contact ERCD to activate options | 1bit BOOL | DI |  | 0 | 1 | 0
0x00D2 | 210 | 1 | ALM_RUN_OUT_MAP_A_F | Compressor Running Outside MAP - cir A | 1bit BOOL | DI |  | 0 | 1 | 0
0x00D3 | 211 | 1 | ALM_RUN_OUT_MAP_B_F | Compressor Running Outside MAP - cir B | 1bit BOOL | DI |  | 0 | 1 | 0
0x07D1 | 2001 | 1 | ALM_DP_A_F | Circuit A Discharge Pressure Transducer Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x07D2 | 2002 | 1 | ALM_DP_B_F | Circuit B Discharge Pressure Transducer Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x07D4 | 2004 | 1 | ALM_SP_A_F | Circuit A Suction Pressure Transducer Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x07D5 | 2005 | 1 | ALM_SP_B_F | Circuit B Suction Pressure Transducer Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x07E8 | 2024 | 1 | ALM_WP_IN_F | Water Exchanger Entering Fluid Transducer Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x07E9 | 2025 | 1 | ALM_WP_OUT_F | Water Exchanger Leaving Fluid Transducer Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x0BB8 | 3000 | 1 | ALM_INI_FACT_CONF_F | Initial factory configuration required | 1bit BOOL | DI |  | 0 | 1 | 0
0x0BB9 | 3001 | 1 | ALM_ILL_FACT_CONF_F | Illegal configuration | 1bit BOOL | DI |  | 0 | 1 | 0
0x0BBA | 3002 | 1 | ALM_ILL_BRAND | Illegal Brand identifier | 1bit BOOL | DI |  | 0 | 0 | 0
0x0C1D | 3101 | 1 | ALM_SERVICE_MAINT_ALERT | Service maintenance alert | 1bit BOOL | DI |  | 0 | 1 | 0
0x0C21 | 3105 | 1 | ALM_FGAS_NEEDED | Fgas check needed, call your maintenance company | 1bit BOOL | DI |  | 0 | 1 | 0
0x0C82 | 3202 | 1 | ALM_WL_PRESS_Z_ERROR_F | Cooler Water Loop : Delta Pressure Error | 1bit BOOL | DI |  | 0 | 1 | 0
0x0C83 | 3203 | 1 | ALM_WL_PRESS_TOO_LOW_F | Cooler Water Loop : Pressure Too Low | 1bit BOOL | DI |  | 0 | 1 | 0
0x0C84 | 3204 | 1 | ALM_WL_PUMP_NO_START_F | Cooler Water Loop : Pump Not Started | 1bit BOOL | DI |  | 0 | 1 | 0
0x0C85 | 3205 | 1 | ALM_WL_PRESS_ERR_RTST_F | Cooler Water Loop : Pressure Error During Runtest | 1bit BOOL | DI |  | 0 | 1 | 0
0x0C86 | 3206 | 1 | ALM_WL_PUMP_OVERLOAD_F | Cooler Water Loop : Pump Overload | 1bit BOOL | DI |  | 0 | 1 | 0
0x0C87 | 3207 | 1 | ALM_WL_LOW_FLOW_F | Cooler Water Loop : Flow Too Low | 1bit BOOL | DI |  | 0 | 1 | 0
0x0C88 | 3208 | 1 | ALM_WL_PRESS_CROSS_F | Cooler Water Loop : Pressure Sensors Crossed | 1bit BOOL | DI |  | 0 | 1 | 0
0x0C89 | 3209 | 1 | ALM_WL_LOW_PRESS_WARN_F | Cooler Water Loop : Low Pressure Warning | 1bit BOOL | DI |  | 0 | 1 | 0
0x0CE5 | 3301 | 1 | ALM_M_S_CONFIG_F | Master chiller configuration error | 1bit BOOL | DI |  | 0 | 1 | 0
0x0FA1 | 4001 | 1 | ALM_SIOB_A_LOW_VOLT_F | Circuit A SIOB Low Voltage Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x0FA2 | 4002 | 1 | ALM_SIOB_B_LOW_VOLT_F | Circuit B SIOB Low Voltage Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x11F9 | 4601 | 1 | ALM_AUX1_COM_F | Loss of communication with AUX1 Board | 1bit BOOL | DI |  | 0 | 1 | 0
0x11FA | 4602 | 1 | ALM_FC_AUX1_COM_F | Loss of communication with Free Cooling Board 1 | 1bit BOOL | DI |  | 0 | 1 | 0
0x125D | 4701 | 1 | ALM_FAN_DRIVE_A_COM_F | Loss of communication with VFD Fan Drive 1 Circuit A | 1bit BOOL | DI |  | 0 | 1 | 0
0x125E | 4702 | 1 | ALM_FAN_DRIVE_A2_COM_F | Loss of communication with VFD Fan Drive 2 Circuit A | 1bit BOOL | DI |  | 0 | 1 | 0
0x125F | 4703 | 1 | ALM_FAN_DRIVE_B_COM_F | Loss of communication with VFD Fan Drive 1 Circuit B | 1bit BOOL | DI |  | 0 | 1 | 0
0x1261 | 4705 | 1 | ALM_PUMP_DRIVE_1_COM_F | Loss of communication with VFD Pump Drive Number 1 | 1bit BOOL | DI |  | 0 | 1 | 0
0x1325 | 4901 | 1 | ALM_SIOB_CIR_A_COM_F | Loss of communication with SIOB Board Number A | 1bit BOOL | DI |  | 0 | 1 | 0
0x1326 | 4902 | 1 | ALM_SIOB_CIR_B_COM_F | Loss of communication with SIOB Board Number B | 1bit BOOL | DI |  | 0 | 1 | 0
0x1389 | 5001 | 1 | ALM_COOL_EWT_F | Water Exchanger Entering Fluid Thermistor Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x138A | 5002 | 1 | ALM_COOL_LWT_F | Water Exchanger Leaving Fluid Thermistor Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x138B | 5003 | 1 | ALM_DEFROST_T_A_F | Circuit A Defrost Thermistor Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x138C | 5004 | 1 | ALM_DEFROST_T_B_F | Circuit B Defrost Thermistor Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x1392 | 5010 | 1 | ALM_OAT_F | OAT Thermistor Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x1393 | 5011 | 1 | ALM_CHWSTEMP_F | MASTER/Slave Common Fluid Thermistor Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x1394 | 5012 | 1 | ALM_SUCTION_T_A_F | Circuit A Suction Gas Thermistor Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x1395 | 5013 | 1 | ALM_SUCTION_T_B_F | Circuit B Suction Gas Thermistor Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x1397 | 5015 | 1 | ALM_DGT_A_F | Circuit A Discharge Gas Thermistor Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x13B4 | 5044 | 1 | ALM_SGTC1_F | Coil Suction Gas Thermistor Sensor 1 Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x13B5 | 5045 | 1 | ALM_SGTC2_F | Coil Suction Gas Thermistor Sensor 2 Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x13B6 | 5046 | 1 | ALM_FC_WLOOP_F | Free Cooling Water Loop Thermistor Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x13B7 | 5047 | 1 | ALM_FC_LWT_F | Free Cooling Leaving Water Thermistor Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x13B8 | 5048 | 1 | ALM_FC_OAT_F | Free Cooling OAT Sensor Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x13BD | 5053 | 1 | ALM_WTOT_F | Water Tank Output Thermistor Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x1771 | 6001 | 1 | ALM_FAN_VFD_DRIVE_A_F | Circuit A VFD Fan Drive 1 Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x17D5 | 6101 | 1 | ALM_FAN_VFD_DRIVE_A2_F | Circuit A VFD Fan Drive 2 Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x1839 | 6201 | 1 | ALM_FAN_VFD_DRIVE_B_F | Circuit B VFD Fan Drive 1 Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x1901 | 6401 | 1 | ALM_PUMP_VFD_DRIVE_1_F | VFD Pump 1 Drive Failure | 1bit BOOL | DI |  | 0 | 1 | 0
0x0384 | 900 | 2 | SETPOINT_csp1 | Cooling Setpoint 1 | 16bits FLOAT | HR | °F | -20 | 68 | 44.6
[7 empty] | °C | -28.8889 | 20 | 7
0x0386 | 902 | 2 | SETPOINT_csp2 | Cooling Setpoint 2 | 16bits FLOAT | HR | °F | -20 | 68 | 44.6
[7 empty] | °C | -28.8889 | 20 | 7
0x038A | 906 | 2 | SETPOINT_hsp1 | Heating Setpoint 1 | 16bits FLOAT | HR | °F | 77 | 131 | 100.4
[7 empty] | °C | 25 | 55 | 38
0x038C | 908 | 2 | SETPOINT_hsp2 | Heating Setpoint 2 | 16bits FLOAT | HR | °F | 77 | 131 | 100.4
[7 empty] | °C | 25 | 55 | 38
0x038E | 910 | 1 | SETPOINT_lim_sp1 | Switch Limit Setpoint 1 | 16bits UINT | HR | PERCENT | 0 | 100 | 100
0x0390 | 912 | 1 | SETPOINT_lim_sp2 | Switch Limit Setpoint 2 | 16bits UINT | HR | PERCENT | 0 | 100 | 100
0x0392 | 914 | 1 | SETPOINT_lim_sp3 | Switch Limit Setpoint 3 | 16bits UINT | HR | PERCENT | 0 | 100 | 100
0x0BC2 | 3010 | 2 | PROTOCOL_CTRL_PNT | Control Point | 16bits FLOAT | HR | °F | -4 | 153 | 44.6
[7 empty] | °C | -20 | 67.2222 | 7
0x0BC6 | 3014 | 1 | PROTOCOL_DEM_LIM | Demand Limit | 16bits UINT | HR | PERCENT | 0 | 100 | 0
0x0BCE | 3022 | 1 | PROTOCOL_CHIL_S_S | Net.: Cmd Start/Stop | 16bits UINT | HR |  | 0 | 1 | 0
0x0BD0 | 3024 | 1 | PROTOCOL_EMSTOP | Emergency Stop | 16bits UINT | HR |  | 0 | 1 | 0
0x0BE4 | 3044 | 1 | PROTOCOL_HC_SEL | Heatcool Select | 16bits UINT | HR |  | 0 | 3 | 0
0x0BE6 | 3046 | 1 | PROTOCOL_SP_SEL | Setpoint Select | 16bits UINT | HR |  | 0 | 2 | 0
0x0C1A | 3098 | 1 | PROTOCOL_PUMP_1 | Evaporator pump 1 | 16bits UINT | HR |  | 0 | 1 | 0
0x0C1C | 3100 | 1 | PROTOCOL_PUMP_2 | Evaporator pump 2 | 16bits UINT | HR |  | 0 | 1 | 0
0x0C2A | 3114 | 1 | PROTOCOL_CHIL_OCC | Chiller occupied? | 16bits UINT | HR |  | 0 | 1 | 0
0x0C2C | 3116 | 1 | PROTOCOL_SP_OCC | Setpoint Occupied? | 16bits UINT | HR |  | 0 | 1 | 0
0x0C4E | 3150 | 1 | PROTOCOL_ROT_PUMP | Rotate Cooler Pumps ? | 16bits UINT | HR |  | 0 | 1 | 0
0x0FA0 | 4000 | 1 | MODBUSRS_metric | Metric Unit | 16bits UINT | HR |  | 0 | 1 | 1
0x0FA2 | 4002 | 1 | MODBUSRS_real_typ | Real type management | 16bits UINT | HR |  | 0 | 1 | 1
0x0FA4 | 4004 | 1 | MODBUSRS_swap_b | Swap Bytes | 16bits UINT | HR |  | 0 | 1 | 0
0x0FA6 | 4006 | 1 | MODBUSIP_metric | Metric Unit | 16bits UINT | HR |  | 0 | 1 | 1
0x0FA8 | 4008 | 1 | MODBUSIP_real_typ | Real type management | 16bits UINT | HR |  | 0 | 1 | 1
0x0FAA | 4010 | 1 | MODBUSIP_swap_b | Swap Bytes | 16bits UINT | HR |  | 0 | 1 | 0
0x1068 | 4200 | 2 | RESETCFG_cr_deg | Cooling Reset Deg. Value | 16bits FLOAT | HR | ^F | -30 | 30 | 0
[7 empty] | ^C | -16.6667 | 16.6667 | 0
0x106A | 4202 | 1 | HCCONFIG_cr_sel | Cooling Reset Select | 16bits UINT | HR |  | 0 | 3 | 0
0x106C | 4204 | 2 | RESETCFG_dt_cr_fu | Delta T Full Reset Value | 16bits FLOAT | HR | ^F | 0 | 25 | 0
[7 empty] | ^C | 0 | 13.8889 | 0
0x106E | 4206 | 2 | RESETCFG_dt_cr_no | Delta T No Reset Value | 16bits FLOAT | HR | ^F | 0 | 25 | 0
[7 empty] | ^C | 0 | 13.8889 | 0
0x1070 | 4208 | 2 | RESETCFG_dt_hr_fu | Delta T Full Reset Value | 16bits FLOAT | HR | ^F | 0 | 25 | 0
[7 empty] | ^C | 0 | 13.8889 | 0
0x1072 | 4210 | 2 | RESETCFG_dt_hr_no | Delta T No Reset Value | 16bits FLOAT | HR | ^F | 0 | 25 | 0
[7 empty] | ^C | 0 | 13.8889 | 0
0x1074 | 4212 | 2 | RESETCFG_hr_deg | Heating Reset Deg. Value | 16bits FLOAT | HR | ^F | -30 | 30 | 0
[7 empty] | ^C | -16.6667 | 16.6667 | 0
0x1076 | 4214 | 1 | HCCONFIG_hr_sel | Heating Reset Select | 16bits UINT | HR |  | 0 | 3 | 0
0x1078 | 4216 | 2 | RESETCFG_oat_crfu | OAT Full Reset Value | 16bits FLOAT | HR | °F | 14 | 125 | 14
[7 empty] | °C | -10 | 51.6667 | -10
0x107A | 4218 | 2 | RESETCFG_oat_crno | OAT No Reset Value | 16bits FLOAT | HR | °F | 14 | 125 | 14
[7 empty] | °C | -10 | 51.6667 | -10
0x107C | 4220 | 2 | RESETCFG_oat_hrfu | OAT Full Reset Value | 16bits FLOAT | HR | °F | 14 | 125 | 14
[7 empty] | °C | -10 | 51.6667 | -10
0x107E | 4222 | 2 | RESETCFG_oat_hrno | OAT No Reset Value | 16bits FLOAT | HR | °F | 14 | 125 | 14
[7 empty] | °C | -10 | 51.6667 | -10
0x1088 | 4232 | 2 | RESETCFG_I_cr_fu | Current Full Reset Value | 16bits FLOAT | HR | MILLIAMPS | 0 | 20 | 0
0x108A | 4234 | 2 | RESETCFG_I_cr_no | Current No Reset Value | 16bits FLOAT | HR | MILLIAMPS | 0 | 20 | 0
0x108C | 4236 | 2 | RESETCFG_I_hr_fu | Current Full Reset Value | 16bits FLOAT | HR | MILLIAMPS | 0 | 20 | 0
0x108E | 4238 | 2 | RESETCFG_I_hr_no | Current No Reset Value | 16bits FLOAT | HR | MILLIAMPS | 0 | 20 | 0
0x10CC | 4300 | 1 | PUMPCONF_pump_seq | Cooler Pumps Sequence | 16bits UINT | HR |  | 0 | 4 | 0
0x10CE | 4302 | 1 | PUMPCONF_pump_del | Pump Auto Rotation Delay | 16bits INT | HR | HOURS | 24 | 3000 | 48
0x10D0 | 4304 | 1 | PUMPCONF_pump_loc | Flow Checked if Pump Off | 16bits UINT | HR |  | 0 | 1 | 1
0x10D2 | 4306 | 1 | PUMPCONF_pump_per | Pump Sticking Protection | 16bits UINT | HR |  | 0 | 1 | 0
0x10D4 | 4308 | 1 | PUMPCONF_pump_sby | Stop Pump During Standby | 16bits UINT | HR |  | 0 | 1 | 0
0x232C | 9004 | 2 | SETPOINT_ramp_sp | Ramp Loading | 16bits FLOAT | HR | ^F | 0.2 | 2 | 1
[7 empty] | ^C | 0.11111 | 1.1111 | 0.55556
0x232E | 9006 | 2 | SETPOINT_cauto_sp | Cool Changeover Setpt | 16bits FLOAT | HR | °F | 39 | 122 | 75
[7 empty] | °C | 3.8889 | 50 | 23.8889
0x2330 | 9008 | 2 | SETPOINT_hauto_sp | Heat Changeover Setpt | 16bits FLOAT | HR | °F | 32 | 115 | 64
[7 empty] | °C | 1.2e-06 | 46.1111 | 17.7778
0x2332 | 9010 | 2 | SETPOINT_min_sct | Desuperheater Min Sct | 16bits FLOAT | HR | °F | 80 | 140 | 104
[7 empty] | °C | 26.6667 | 60 | 40
0x238C | 9100 | 1 | OPT_SEL_boil_en | Boiler Enable | 16bits UINT | HR |  | 0 | 1 | 0
0x238E | 9102 | 1 | OPT_SEL_ehs_en | EHS Number | 16bits UINT | HR |  | 0 | 4 | 0
0x2390 | 9104 | 1 | OPT_SEL_fc_en | DC Free Cooling Enable | 16bits UINT | HR |  | 0 | 2 | 0
0x0000 | 0 | 2 | TEMP_EWT | Entering Water Temp | 16bits FLOAT | IR | °F |  |  | 0
[7 empty] | °C |  |  | -17.7778
0x0002 | 2 | 2 | TEMP_LWT | Leaving Water Temp | 16bits FLOAT | IR | °F |  |  | 0
[7 empty] | °C |  |  | -17.7778
0x0004 | 4 | 2 | TEMP_OAT | Outdoor Air Temperature | 16bits FLOAT | IR | °F | -40 | 302 | 0
[7 empty] | °C | -40 | 150 | -17.7778
0x0008 | 8 | 2 | TEMP_CHWSTEMP | Cold Water System Temp | 16bits FLOAT | IR | °F | -40 | 302 | 0
[7 empty] | °C | -40 | 150 | -17.7778
0x000A | 10 | 2 | GENUNIT_CTRL_PNT | Control Point | 16bits FLOAT | IR | °F | -4 | 153 | 0
[7 empty] | °C | -20 | 67.2222 | -17.7778
0x000C | 12 | 2 | GENUNIT_SP | Current Setpoint | 16bits FLOAT | IR | °F |  |  | 0
[7 empty] | °C |  |  | -17.7778
0x000E | 14 | 1 | GENUNIT_DEM_LIM | Active Demand Limit Val | 16bits UINT | IR | PERCENT | 0 | 100 | 0
0x0010 | 16 | 1 | GENUNIT_CAP_T | Percent Total Capacity | 16bits UINT | IR | PERCENT | 0 | 100 | 0
0x0014 | 20 | 2 | GENUNIT_min_left | Minutes Left for Start | 16bits FLOAT | IR | MINUTES |  |  | 0
0x0016 | 22 | 1 | GENUNIT_CHIL_S_S | Net.: Cmd Start/Stop | 16bits UINT | IR |  | 0 | 1 | 0
0x0018 | 24 | 1 | GENUNIT_EMSTOP | Emergency Stop | 16bits UINT | IR |  | 0 | 1 | 0
0x001C | 28 | 1 | OUTPUTS_RUN | Running Relay | 16bits UINT | IR |  |  |  | 0
0x001E | 30 | 1 | INPUTS_ONOFF_SW | Remote On/Off Switch | 16bits UINT | IR |  | 0 | 1 | 0
0x0022 | 34 | 1 | INPUTS_LIM_SW1 | Limit Switch 1 | 16bits UINT | IR |  | 0 | 1 | 0
0x0024 | 36 | 1 | INPUTS_LIM_SW2 | Limit Switch 2 | 16bits UINT | IR |  | 0 | 1 | 0
0x0028 | 40 | 1 | GENUNIT_CTRL_TYP | Local=0 Net.=1 Remote=2 | 16bits UINT | IR |  | 0 | 2 | 0
0x002A | 42 | 1 | UNIT_STATUS | Running Status | 16bits UINT | IR |  |  |  | 0
0x002C | 44 | 1 | GENUNIT_HC_SEL | Heat/Cool Select | 16bits UINT | IR |  | 0 | 2 | 0
0x002E | 46 | 1 | GENUNIT_SP_SEL | Setpoint Select | 16bits UINT | IR |  | 0 | 2 | 0
0x0048 | 72 | 2 | PRESSURE_PUMP_EWP | Entering Water Pressure | 16bits FLOAT | IR | PSI |  |  | 0
[7 empty] | kPa |  |  | 0
0x004A | 74 | 2 | PRESSURE_PUMP_LWP | Leaving Water Pressure | 16bits FLOAT | IR | PSI |  |  | 0
[7 empty] | kPa |  |  | 0
0x0054 | 84 | 1 | INPUTS_ELEC_BOX | Electrical Box Failure | 16bits UINT | IR |  | 0 | 1 | 0
0x005E | 94 | 1 | INPUTS_SETP_SW | Second Setpoint Switch | 16bits UINT | IR |  | 0 | 1 | 0
0x0062 | 98 | 1 | PUMPSTAT_PUMP_1 | Water Pump #1 | 16bits UINT | IR |  | 0 | 1 | 0
0x0064 | 100 | 1 | PUMPSTAT_PUMP_2 | Water Pump #2 | 16bits UINT | IR |  | 0 | 1 | 0
0x0066 | 102 | 1 | INPUTS_FLOW_SW | Flow Switch Interlock | 16bits UINT | IR |  | 0 | 1 | 0
0x0070 | 112 | 1 | OUTPUTS_EXCH_HTR | Exchanger Heater | 16bits UINT | IR |  |  |  | 0
0x0072 | 114 | 1 | GENUNIT_CHIL_OCC | Net.: Cmd Occupied | 16bits UINT | IR |  | 0 | 1 | 0
0x0074 | 116 | 1 | GENUNIT_SP_OCC | Setpoint Occupied? | 16bits UINT | IR |  | 0 | 1 | 0
0x008A | 138 | 2 | PUMPSTAT_VPMP_CMD | Variable Pump Command | 16bits FLOAT | IR | PERCENT |  |  | 0
0x008C | 140 | 2 | PUMPSTAT_WAT_FLOW | Water Flow | 16bits FLOAT | IR | GPS |  |  | 0
[7 empty] | l/s |  |  | 0
0x0090 | 144 | 1 | PUMPCONF_pump_seq | Cooler Pumps Sequence | 16bits UINT | IR |  | 0 | 4 | 0
0x0096 | 150 | 1 | PUMPSTAT_ROT_PUMP | Rotate Pumps Now? | 16bits UINT | IR |  | 0 | 1 | 0
0x03E8 | 1000 | 2 | RUNTIME_hr_mach | Machine Operating Hours | 16bits FLOAT | IR | HOURS |  |  | 0
0x03EA | 1002 | 2 | RUNTIME_st_mach | Machine Starts Number | 16bits FLOAT | IR |  |  |  | 0
0x03EC | 1004 | 2 | RUNTIME_hr_pump1 | Water Pump #1 Hours | 16bits FLOAT | IR | HOURS |  |  | 0
0x03EE | 1006 | 2 | RUNTIME_hr_pump2 | Water Pump #2 Hours | 16bits FLOAT | IR | HOURS |  |  | 0
0x03F4 | 1012 | 2 | HR_PARTIAL_DOWNTIME | Cumul Time Partial Alm | 16bits FLOAT | IR | HOURS |  |  | 0
0x03F6 | 1014 | 2 | HR_TOTAL_DOWNTIME | Cumul Time Tripout Alm | 16bits FLOAT | IR | HOURS |  |  | 0
0x044C | 1100 | 1 | ALARMRST_alarm_1c | Current Alarm 1 | 16bits UINT | IR |  |  |  | 0
0x044E | 1102 | 1 | ALARMRST_alarm_2c | Current Alarm 2 | 16bits UINT | IR |  |  |  | 0
0x0450 | 1104 | 1 | ALARMRST_alarm_3c | Current Alarm 3 | 16bits UINT | IR |  |  |  | 0
0x0452 | 1106 | 1 | ALARMRST_alarm_4c | Current Alarm 4 | 16bits UINT | IR |  |  |  | 0
0x0454 | 1108 | 1 | ALARMRST_alarm_5c | Current Alarm 5 | 16bits UINT | IR |  |  |  | 0
0x0456 | 1110 | 1 | ALARMRST_alarm_1 | Current Alarm 1 index | 16bits UINT | IR |  |  |  | 0
0x0458 | 1112 | 1 | ALARMRST_alarm_2 | Current Alarm 2 index | 16bits UINT | IR |  |  |  | 0
0x045A | 1114 | 1 | ALARMRST_alarm_3 | Current Alarm 3 index | 16bits UINT | IR |  |  |  | 0
0x045C | 1116 | 1 | ALARMRST_alarm_4 | Current Alarm 4 index | 16bits UINT | IR |  |  |  | 0
0x045E | 1118 | 1 | ALARMRST_alarm_5 | Current Alarm 5 index | 16bits UINT | IR |  |  |  | 0
0x0460 | 1120 | 1 | UNIT_ALM | Alarm Status | 16bits UINT | IR |  |  |  | 0
0x04B0 | 1200 | 2 | PRESSURE_DP_A | Discharge Pressure A | 16bits FLOAT | IR | PSI |  |  | 0
[7 empty] | kPa |  |  | 0
0x04B2 | 1202 | 2 | PRESSURE_SP_A | Suction Pressure A | 16bits FLOAT | IR | PSI |  |  | 0
[7 empty] | kPa |  |  | 0
0x04BA | 1210 | 2 | TEMP_SCT_A | Saturated Cond Tmp cir A | 16bits FLOAT | IR | °F |  |  | 0
[7 empty] | °C |  |  | -17.7778
0x04BC | 1212 | 2 | TEMP_SST_A | Saturated Suction Temp A | 16bits FLOAT | IR | °F |  |  | 0
[7 empty] | °C |  |  | -17.7778
0x04BE | 1214 | 2 | TEMP_SUCT_A | Suction Temp Circuit A | 16bits FLOAT | IR | °F |  |  | 0
[7 empty] | °C |  |  | -17.7778
0x04C2 | 1218 | 2 | TEMP_DGT_A | Discharge Gas Temp A | 16bits FLOAT | IR | °F |  |  | 0
[7 empty] | °C |  |  | -17.7778
0x04CE | 1230 | 2 | OUTPUTS_VFAN_A | VariaFan Speed A | 16bits FLOAT | IR | PERCENT |  |  | 0
0x04D2 | 1234 | 1 | GENUNIT_CAPA_T | Circuit A Total Capacity | 16bits UINT | IR | PERCENT | 0 | 100 | 0
0x04F0 | 1264 | 1 | OUTPUTS_CP_A1 | Compressor A1 | 16bits UINT | IR |  |  |  | 0
0x04F2 | 1266 | 1 | OUTPUTS_CP_A2 | Compressor A2 | 16bits UINT | IR |  |  |  | 0
0x04F4 | 1268 | 1 | OUTPUTS_CP_A3 | Compressor A3 | 16bits UINT | IR |  |  |  | 0
0x0500 | 1280 | 2 | TEMP_DEFRT_A | Defrost Temp Circuit A | 16bits FLOAT | IR | °F |  |  | 0
[7 empty] | °C |  |  | -17.7778
0x0502 | 1282 | 2 | TEMP_DEFRT_A2 | Defrost Temp A Coil 2 | 16bits FLOAT | IR | °F |  |  | 0
[7 empty] | °C |  |  | -17.7778
0x0514 | 1300 | 1 | OUTPUTS_FAN_A1LS | Fan A1 Low Speed | 16bits UINT | IR |  |  |  | 0
0x0516 | 1302 | 1 | OUTPUTS_FAN_A1HS | Fan A1 High Speed | 16bits UINT | IR |  |  |  | 0
0x0518 | 1304 | 1 | OUTPUTS_FAN_A2LS | Fan A2 Low Speed | 16bits UINT | IR |  |  |  | 0
0x051A | 1306 | 1 | OUTPUTS_FAN_A2HS | Fan A2 High Speed | 16bits UINT | IR |  |  |  | 0
0x0578 | 1400 | 2 | PRESSURE_DP_B | Discharge Pressure B | 16bits FLOAT | IR | PSI |  |  | 0
[7 empty] | kPa |  |  | 0
0x057A | 1402 | 2 | PRESSURE_SP_B | Suction Pressure B | 16bits FLOAT | IR | PSI |  |  | 0
[7 empty] | kPa |  |  | 0
0x0582 | 1410 | 2 | TEMP_SCT_B | Saturated Cond Tmp cir B | 16bits FLOAT | IR | °F |  |  | 0
[7 empty] | °C |  |  | -17.7778
0x0584 | 1412 | 2 | TEMP_SST_B | Saturated Suction Temp B | 16bits FLOAT | IR | °F |  |  | 0
[7 empty] | °C |  |  | -17.7778
0x0586 | 1414 | 2 | TEMP_SUCT_B | Suction Temp Circuit B | 16bits FLOAT | IR | °F |  |  | 0
[7 empty] | °C |  |  | -17.7778
0x058A | 1418 | 2 | TEMP_DGT_B | Discharge Gas Temp B | 16bits FLOAT | IR | °F |  |  | 0
[7 empty] | °C |  |  | -17.7778
0x0596 | 1430 | 2 | OUTPUTS_VFAN_B | VariaFan Speed B | 16bits FLOAT | IR | PERCENT |  |  | 0
0x059A | 1434 | 1 | GENUNIT_CAPB_T | Circuit B Total Capacity | 16bits UINT | IR | PERCENT | 0 | 100 | 0
0x05B8 | 1464 | 1 | OUTPUTS_CP_B1 | Compressor B1 | 16bits UINT | IR |  |  |  | 0
0x05BA | 1466 | 1 | OUTPUTS_CP_B2 | Compressor B2 | 16bits UINT | IR |  |  |  | 0
0x05C8 | 1480 | 2 | TEMP_DEFRT_B | Defrost Temp Circuit B | 16bits FLOAT | IR | °F |  |  | 0
[7 empty] | °C |  |  | -17.7778
0x05DC | 1500 | 1 | OUTPUTS_FAN_B1LS | Fan B1 Low Speed | 16bits UINT | IR |  |  |  | 0
0x05DE | 1502 | 1 | OUTPUTS_FAN_B1HS | Fan B1 High Speed | 16bits UINT | IR |  |  |  | 0
0x0708 | 1800 | 2 | RUNTIME_hr_cp_a1 | Compressor A1 Hours | 16bits FLOAT | IR | HOURS |  |  | 0
0x070A | 1802 | 2 | RUNTIME_hr_cp_a2 | Compressor A2 Hours | 16bits FLOAT | IR | HOURS |  |  | 0
0x070C | 1804 | 2 | RUNTIME_hr_cp_a3 | Compressor A3 Hours | 16bits FLOAT | IR | HOURS |  |  | 0
0x0710 | 1808 | 2 | RUNTIME_st_cp_a1 | Compressor A1 Starts | 16bits FLOAT | IR |  |  |  | 0
0x0712 | 1810 | 2 | RUNTIME_st_cp_a2 | Compressor A2 Starts | 16bits FLOAT | IR |  |  |  | 0
0x0714 | 1812 | 2 | RUNTIME_st_cp_a3 | Compressor A3 Starts | 16bits FLOAT | IR |  |  |  | 0
0x071A | 1818 | 2 | RUNTIME_hr_fana1 | Circuit A Fan #1 Hours | 16bits FLOAT | IR | HOURS |  |  | 0
0x071C | 1820 | 2 | RUNTIME_hr_fana2 | Circuit A Fan #2 Hours | 16bits FLOAT | IR | HOURS |  |  | 0
0x0736 | 1846 | 2 | RUNTIME_st_fana1 | Circuit A Fan #1 Starts | 16bits FLOAT | IR |  |  |  | 0
0x0738 | 1848 | 2 | RUNTIME_st_fana2 | Circuit A Fan #2 Starts | 16bits FLOAT | IR |  |  |  | 0
0x073A | 1850 | 2 | RUNTIME_nb_defra | Circuit A Defrost Number | 16bits FLOAT | IR |  |  |  | 0
0x07D0 | 2000 | 2 | RUNTIME_hr_cp_b1 | Compressor B1 Hours | 16bits FLOAT | IR | HOURS |  |  | 0
0x07D2 | 2002 | 2 | RUNTIME_hr_cp_b2 | Compressor B2 Hours | 16bits FLOAT | IR | HOURS |  |  | 0
0x07D8 | 2008 | 2 | RUNTIME_st_cp_b1 | Compressor B1 Starts | 16bits FLOAT | IR |  |  |  | 0
0x07DA | 2010 | 2 | RUNTIME_st_cp_b2 | Compressor B2 Starts | 16bits FLOAT | IR |  |  |  | 0
0x07E2 | 2018 | 2 | RUNTIME_hr_fanb1 | Circuit B Fan #1 Hours | 16bits FLOAT | IR | HOURS |  |  | 0
0x07FE | 2046 | 2 | RUNTIME_st_fanb1 | Circuit B Fan #1 Starts | 16bits FLOAT | IR |  |  |  | 0
0x0802 | 2050 | 2 | RUNTIME_nb_defrb | Circuit B Defrost Number | 16bits FLOAT | IR |  |  |  | 0
0x2328 | 9000 | 1 | FACTORY_unit_typ | Unit Type (HeatPump = 2) | 16bits UINT | IR |  | 1 | 2 | 1
0x232A | 9002 | 1 | FACTORY_unitsize | Unit Capacity Model | 16bits UINT | IR |  |  |  | 0
0x2334 | 9012 | 2 | TEMP_sgtc1 | Suction Gas Temp Coil 1 | 16bits FLOAT | IR | °F |  |  | 0
[7 empty] | °C |  |  | -17.7778
0x2338 | 9016 | 2 | TEMP_sgtc2 | Suction Gas Temp Coil 2 | 16bits FLOAT | IR | °F |  |  | 0
[7 empty] | °C |  |  | -17.7778
0x233A | 9018 | 2 | TEMP_wtot | Water Tank Output Temp | 16bits FLOAT | IR | °F |  |  | 0
[7 empty] | °C |  |  | -17.7778
0x233C | 9020 | 1 | OUTPUTS_RV_A | 4 Way Refrigerant ValveA | 16bits UINT | IR |  |  |  | 0
0x233E | 9022 | 1 | OUTPUTS_RV_B | 4 Way Refrigerant ValveB | 16bits UINT | IR |  |  |  | 0
0x2340 | 9024 | 2 | OUTPUTS_EXV_A | EXV Position Circuit A | 16bits FLOAT | IR | PERCENT |  |  | 0
0x2342 | 9026 | 2 | OUTPUTS_EXV_B | EXV Position Circuit B | 16bits FLOAT | IR | PERCENT |  |  | 0
0x2344 | 9028 | 1 | OUTPUTS_BOILER | Boiler Command | 16bits UINT | IR |  |  |  | 0
0x2346 | 9030 | 1 | OUTPUTS_EHS_STEP | Electrical Heat Stage | 16bits UINT | IR |  |  |  | 0
0x2348 | 9032 | 1 | OUTPUTS_tnk_hpow | Water Tank EHS power | 16bits UINT | IR | KW |  |  | 0
0x234A | 9034 | 1 | OUTPUTS_OIL_VALV | Oil Valve Status | 16bits UINT | IR |  |  |  | 0
0x234C | 9036 | 2 | PUMPSTAT_W_P_IN | Inlet Water Pressure | 16bits FLOAT | IR | PSI |  |  | 0
[7 empty] | kPa |  |  | 0
0x234E | 9038 | 2 | PUMPSTAT_W_P_OUT | Outlet Water Pressure | 16bits FLOAT | IR | PSI |  |  | 0
[7 empty] | kPa |  |  | 0
0x2350 | 9040 | 2 | PUMPSTAT_DP_FILTR | Delta Water Press. Filt | 16bits FLOAT | IR | PSI |  |  | 0
[7 empty] | kPa |  |  | 0
0x2352 | 9042 | 2 | PUMPSTAT_WP_MIN | Mini Water Pressure | 16bits FLOAT | IR | PSI |  |  | 0
[7 empty] | kPa |  |  | 0
0x2354 | 9044 | 2 | PUMPSTAT_CAPPOWER | Actual Power Capacity | 16bits FLOAT | IR | KW |  |  | 0
0x2356 | 9046 | 2 | PUMPSTAT_p_dt_spt | Water DT Setpoint | 16bits FLOAT | IR | ^F |  |  | 0
[7 empty] | ^C |  |  | 0
0x2358 | 9048 | 2 | PUMPSTAT_p_dp_spt | Water DP Setpoint | 16bits FLOAT | IR | PSI |  |  | 0
[7 empty] | kPa |  |  | 0
0x235A | 9050 | 2 | DCFC_STA_oat | OAT Free Cooling | 16bits FLOAT | IR | °F |  |  | 0
[7 empty] | °C |  |  | -17.7778
0x235C | 9052 | 2 | DCFC_STA_lwt | FC Leaving Water Temp | 16bits FLOAT | IR | °F |  |  | 0
[7 empty] | °C |  |  | -17.7778
0x235E | 9054 | 2 | DCFC_STA_wloop | FC Water Loop Temp | 16bits FLOAT | IR | °F |  |  | 0
[7 empty] | °C |  |  | -17.7778
0x2360 | 9056 | 1 | DCFC_STA_m_dcfc | Free Cooling Mode Active | 16bits UINT | IR |  | 0 | 1 | 0
0x2362 | 9058 | 2 | DCFC_STA_dcfc_cap | FC Capacity | 16bits FLOAT | IR | PERCENT | 0 | 100 | 0
0x2364 | 9060 | 1 | DCFC_STA_f_stage | Fix Speed Fans Stage | 16bits UINT | IR |  | 0 | 10 | 0
0x2366 | 9062 | 2 | DCFC_STA_vf_speed | Varifan Speed | 16bits FLOAT | IR | PERCENT | 0 | 100 | 0
0x2368 | 9064 | 2 | DCFC_STA_pid_out | PID Output | 16bits FLOAT | IR | PERCENT | 0 | 100 | 0
0x236A | 9066 | 2 | DCFC_STA_FC_HOUR | DCFC Operating Hours | 16bits FLOAT | IR | HOURS | 0 | 999999 | 0
0x236C | 9068 | 2 | DCFC_STA_FC_FAN1S | DCFC Fan Stage 1 Start | 16bits FLOAT | IR |  | 0 | 999999 | 0
0x236E | 9070 | 2 | DCFC_STA_FC_FAN1H | DCFC Fan Stage 1 Hours | 16bits FLOAT | IR | HOURS | 0 | 999999 | 0
0x2370 | 9072 | 2 | DCFC_STA_FC_FAN2S | DCFC Fan Stage 2 Start | 16bits FLOAT | IR |  | 0 | 999999 | 0
0x2372 | 9074 | 2 | DCFC_STA_FC_FAN2H | DCFC Fan Stage 2 Hours | 16bits FLOAT | IR | HOURS | 0 | 999999 | 0
0x2374 | 9076 | 2 | DCFC_STA_FC_FAN3S | DCFC Fan Stage 3 Start | 16bits FLOAT | IR |  | 0 | 999999 | 0
0x2376 | 9078 | 2 | DCFC_STA_FC_FAN3H | DCFC Fan Stage 3 Hours | 16bits FLOAT | IR | HOURS | 0 | 999999 | 0
0x2378 | 9080 | 2 | DCFC_STA_FC_FAN4S | DCFC Fan Stage 4 Start | 16bits FLOAT | IR |  | 0 | 999999 | 0
0x237A | 9082 | 2 | DCFC_STA_FC_FAN4H | DCFC Fan Stage 4 Hours | 16bits FLOAT | IR | HOURS | 0 | 999999 | 0
0x237C | 9084 | 2 | DCFC_STA_FC_FAN5S | DCFC Fan Stage 5 Start | 16bits FLOAT | IR |  | 0 | 999999 | 0
0x237E | 9086 | 2 | DCFC_STA_FC_FAN5H | DCFC Fan Stage 5 Hours | 16bits FLOAT | IR | HOURS | 0 | 999999 | 0
0x2380 | 9088 | 2 | DCFC_STA_FC_FAN6S | DCFC Fan Stage 6 Start | 16bits FLOAT | IR |  | 0 | 999999 | 0
0x2382 | 9090 | 2 | DCFC_STA_FC_FAN6H | DCFC Fan Stage 6 Hours | 16bits FLOAT | IR | HOURS | 0 | 999999 | 0
0x2384 | 9092 | 2 | DCFC_STA_FC_FAN7S | DCFC Fan Stage 7 Start | 16bits FLOAT | IR |  | 0 | 999999 | 0
0x2386 | 9094 | 2 | DCFC_STA_FC_FAN7H | DCFC Fan Stage 7 Hours | 16bits FLOAT | IR | HOURS | 0 | 999999 | 0
0x2388 | 9096 | 2 | DCFC_STA_FC_VFANS | DCFC Variable Fan Start | 16bits FLOAT | IR |  | 0 | 999999 | 0
0x238A | 9098 | 2 | DCFC_STA_FC_VFANH | DCFC Variable Fan Hours | 16bits FLOAT | IR | HOURS | 0 | 999999 | 0