## Feuil1
REGISTER | JBUS | CONTENT | TYPE** |  | REMARK**
ADDRESS | ACCESS
|  |  | INT | FLOAT
0 [h00] | R | Entering Fluid Temperature |  | X | Read value must be divided by 10
1 [h01] | R | Leaving Fluid Temperature |  | X | Read value must be divided by 10
2 [h02] | R | Circuit A Discharge Pressure |  | X | Read value must be divided by 10
3 [h03] | R | Circuit B Discharge Pressure |  | X | Read value must be divided by 10
4 [h04] | R | Chiller State | X |  | 0 = Off, 1 = On, 6=delay, 24=running
5 [h05] | R | Alarm State | X |  | 0 = Normal, 16 = Partial, 25 = Shutdown
6 [h06] | R | Heat Cool Select | X |  | 0 = cool, 1 = heat
7 [h07] | R | Control Point |  | X | Read value must be divided by 10
8 [h08] | R | Unit Percent Active Capacity | X
9 [h09] | R | Demand Limit | X
10 [h0A] | R | Cooler Pump # 1 status | X
11 [h0B] | R | Cooler Pump #2 status | X
12 [h0C] | R | Machine Operating Hours |  | X
13 [h0D] | R | Compressor A1 Hours |  | X
14 [h0E] | R | Compressor A2 Hours |  | X
15 [h0F] | R | Compressor A3 Hours |  | X
16 [h10] | R | circuit A defrost number |  | X
17 [h11] | R | Compressor A1 Hours |  | X
18 [h12] | R | Compressor A2 Hours |  | X
19 [h13] | R | circuit B defrost number |  | X
20 [h14] | R | Fan A1 hours |  | X
21 [h15] | R | Fan A1 starts |  | X
22 [h16] | R | Fan B1 hours |  | X
23 [h17] | R | Fan B1 starts |  | X
24 [h18] | R | Inlet Water pressure |  | X | Read value must be divided by 10
25 [h19] | R | Outlet Water pressure |  | X | Read value must be divided by 10
26 [h20] | R | Unit Water flow (l/s) |  | x | Read value must be divided by 10
27 [h2A] | R | Unit capacity (kW) |  | X | Read value must be divided by 10
40 [h28] | R | Total Number of active alarms | X
41 [h29] | R | Active alarm 1* | X |  | Provide the active alarm number (index from 1 to nnn). These are stored in arrival order.
Alarms read from CCN/JBUS are alarm index but not alarms (refer to section alarm code & text description)
42 [h2A] | R | Active alarm 2* | X
43 [h2B] | R | Active alarm 3* | X
44 [h2C] | R | Active alarm 4* | X
45 [h2D] | R | Active alarm 5* | X
61 [h3D] | R | Gateway current alarm code | X |  | 2 = CCN communication failure
66 [h42] | R | JBUS alarm code | X
97 [h61] | R/W | Cooling Setpoint 1 |  | X | Write value must be multiplied by 10
98 [h62] | R/W | Cooling Setpoint 2 |  | X | Write value must be multiplied by 10
99 [h63] | R/W | Heating Setpoint 1 |  | X | Write value must be multiplied by 10
100 [h64] | R/W | Heating Setpoint 2 |  | X | Write value must be multiplied by 10
107 [6Bh] | R/W | Chiller Start/Stop *** | X |  | 0 = Off 1 = On
108 [h6C] | R/W | Control Point |  | X | Write value must be multiplied by 10
109 [h6D] | R/W | Demand Limit Value | X
110 [h6E] | R/W | Heat Cool Select | X
112 [70h] | R/W | JBUS baud rate | X |  | Default = 9600
113 [71h] | R/W | JBUS address | X |  | Default = 1