## Base Chiller
Parameter | Type de SNVT | Read/Write | Type | Unit | Format | Value | Précision | Point | CCN Point | CCN Table | Description | Remarks
nviChillerEnable | SNVT_switch | W | Switch (*) |  | 2 bytes |  |  | POINT 01 | CHIL_S_S | GENUNIT | Net.: Cmd Start/Stop
nviCoolSetpt | SNVT_temp_p | W | Temp. / Cons | °C | 2 bytes long signé |  | 0.01 | POINT 02 | CTRL_PNT | GENUNIT | Control Point
nvoOnOff | SNVT_switch | R | Switch (*) |  | 2 bytes |  |  | POINT 03 | CHIL_S_S | GENUNIT | Net.: Cmd Start/Stop
nvoActiveSetpt | SNVT_temp_p | R | Temperature | °C | 2 bytes long signé |  | 0.01 | POINT 04 | SP | GENUNIT | Current Setpoint
nviCapacityLim | SNVT_lev_percent | W | Percent / Con. | % | 2 bytes long signé |  | 0.005 | POINT 05 | DEM_LIM | GENUNIT | Active Demand Limit Val
nviHeatSept | SNVT_temp_p | W | Temp. / Cons | °C | 2 bytes long signé |  | 0.01 | POINT 06 | hsp1 | SETPOINT | Heating Setpoint 1
nvoActualCapacity | SNVT_lev_percent | R | Percent | % | 2 bytes long signé |  | 0.005 | POINT 07 | CAP_T | GENUNIT | Percent Total Capacity
nvoCapacityLim | SNVT_lev_percent | R | Percent | % | 2 bytes long signé |  | 0.005 | POINT 08 | DEM_LIM | GENUNIT | Active Demand Limit Val
nvoLvgCHWTemp | SNVT_temp_p | R | Temperature | °C | 2 bytes long signé |  | 0.01 | POINT 09 | LWT | TEMP | Leaving Water Temp.
nvoEntCHWTemp | SNVT_temp_p | R | Temperature | °C | 2 bytes long signé |  | 0.01 | POINT 10 | EWT | TEMP | Entering Water Temp.
nvoEntCNDWTemp | SNVT_temp_p | R | Temperature | °C |  |  | 0.01 | POINT 11 | OAT | TEMP | Outside Air Temperature
nvoLvgCNDWTemp | SNVT_temp_p | R | Temperature | °C |  |  | 0.01 | POINT 12 | CHWSTEMP | TEMP | Master/Slave Temperature
nvoChillerStat.run_mode | SNVT_chlr_Status | R | N/A |  |  |  |  | POINT 13
nvoChillerStat.op_mode | SNVT_chlr_Status | R | N/A |  |  |  |  | POINT 14
nvoChillerStat.in_alarm | SNVT_chlr_Status | R | N/A |  |  |  |  | POINT 15
nvoChillerStat.run_enabl | SNVT_chlr_Status | R | N/A |  |  |  |  | POINT 16
nvoChillerStat.Local | SNVT_chlr_Status | R | N/A |  |  |  |  | POINT 17
nvoChillerStat.Limited | SNVT_chlr_Status | R | N/A |  |  |  |  | POINT 18
nvoChillerStat.chw_flow | SNVT_chlr_Status | R | N/A |  |  |  |  | POINT 19
nvoChillerStat.cndw_flow | SNVT_chlr_Status | R | N/A |  |  |  |  | POINT 20
nviOccSchedule | SNVT_tod_event | W | N/A |  |  |  |  | POINT 21
nviTEMP1 | SNVT_temp_p | W | Temp. / Cons | °C | 2 bytes long signé |  | 0.01 | POINT 22 | hsp1 | SETPOINT | Heating Setpoint 1
nvoTEMP1 | SNVT_temp_p | R | Temperature | °C | 2 bytes long signé |  | 0.01 | POINT 23 | hsp2 | SETPOINT | Heating Setpoint 2
nvoTEMP2 | SNVT_temp_p | R | Temperature | °C | 2 bytes long signé |  | 0.01 | POINT 24 | dhw_sp | DHW_CONF | DHW Setpoint
nvoTEMP3 | SNVT_temp_p | R | Temperature | °C | 2 bytes long signé |  | 0.01 | POINT 25 | SCT_A | TEMP | Saturated Condensing Tp
nvoTEMP4 | SNVT_temp_p | R | Temperature | °C | 2 bytes long signé |  | 0.01 | POINT 26 | SST_A | TEMP | Saturated Suction Temp
nvoTEMP5 | SNVT_temp_p | R | Temperature | °C | 2 bytes long signé |  | 0.01 | POINT 27 | ECO_SST | TEMP | Eco. Saturated Suction T
nvoTEMP6 | SNVT_temp_p | R | Temperature | °C | 2 bytes long signé |  | 0.01 | POINT 28
nviPRESS1 | SNVT_press | W | Pressure / Con. | kPa | 2 bytes long signé |  | 0.1 | POINT 29
nvoPRESS1 | SNVT_press | R | Pressure | kPa | 2 bytes long signé |  | 0.1 | POINT 30 | DP_A | PRESSURE | Discharge Pressure
nvoPRESS2 | SNVT_press | R | Pressure | kPa | 2 bytes long signé |  | 0.1 | POINT 31 | SP_A | PRESSURE | Main Suction Pressure
nvoPRESS3 | SNVT_press | R | Pressure | kPa | 2 bytes long signé |  | 0.1 | POINT 32 | ECO_SP_A | PRESSURE | Eco. Suction Pressure
nvoPRESS4 | SNVT_press | R | Pressure | kPa | 2 bytes long signé |  | 0.1 | POINT 33
nvoPCT1 | SNVT_lev_percent | R | Percent | % | 2 bytes long signé |  | 0.005 | POINT 34
nvoPCT2 | SNVT_lev_percent | R | Percent | % | 2 bytes long signé |  | 0.005 | POINT 35
nvoTEMPDIFF1 | SNVT_temp_diff_p | R | N/A |  |  |  |  | POINT 36
nvoTEMPDIFF2 | SNVT_temp_diff_p | R | N/A |  |  |  |  | POINT 37
nviDISCRETE1 | SNVT_switch | W | Switch (*) |  | 2 bytes |  |  | POINT 38 | EMSTOP | GENUNIT | Emergency Stop
nviDISCRETE2 | SNVT_switch | W | Switch (*) |  | 2 bytes |  |  | POINT 39
nvoDISCRETE1 | SNVT_switch | R | Switch (*) |  | 2 bytes |  |  | POINT 40 | EMSTOP | GENUNIT | Emergency Stop
nvoDISCRETE2 | SNVT_switch | R | Switch (*) |  | 2 bytes |  |  | POINT 41 | CHIL_OCC | GENUNIT | Net.: Cmd Occupied
nvoDISCRETE3 | SNVT_switch | R | Switch (*) |  | 2 bytes |  |  | POINT 42 | FLOW_SW | INPUTS | Flow Switch
nvoDISCRETE4 | SNVT_switch | R | Switch (*) |  | 2 bytes |  |  | POINT 43
nvoDISCRETE5 | SNVT_switch | R | Switch (*) |  | 2 bytes |  |  | POINT 44
nvoDISCRETE6 | SNVT_switch | R | Switch (*) |  | 2 bytes |  |  | POINT 45
nviCOUNT1 | SNVT_count | W | event counter |  | 2 bytes long pas signé |  | 1 | POINT 46
nvoCOUNT1 | SNVT_count | R | event counter |  | 2 bytes long pas signé |  | 1 | POINT 47 | ALM | GENUNIT | Alarm
nvoCOUNT2 | SNVT_count | R | event counter |  | 2 bytes long pas signé |  | 1 | POINT 48 | CTRL_TYP | GENUNIT | Local=0 Net.=1 Remote=2
nvoCOUNTinc1 | SNVT_count_inc | R | event counter |  | 2 bytes long pas signé |  | 1 | POINT 49
nvoCOUNTinc2 | SNVT_count_inc | R | event counter |  | 2 bytes long pas signé |  | 1 | POINT 50