## Base Chiller
Parameter | Type de SNVT | Read/Write | Type | Unit | Format | Value | Précision | Point | CCN Point | CCN Table | Description | Remarks
nviChillerEnable | SNVT_switch | W | Switch (*) |  | 2 bytes |  |  | POINT 01 | CHIL_S_S | GENUNIT | 开机/停机指令
nviCoolSetpt | SNVT_temp_p | W | Temp. / Cons | °C | 2 bytes long signé |  | 0.01 | POINT 02 | CTRL_PNT | GENUNIT | 控制点
nvoOnOff | SNVT_switch | R | Switch (*) |  | 2 bytes |  |  | POINT 03 | CHIL_S_S | GENUNIT | 开机/停机指令
nvoActiveSetpt | SNVT_temp_p | R | Temperature | °C | 2 bytes long signé |  | 0.01 | POINT 04 | SP | GENUNIT | 当前设定值
nviCapacityLim | SNVT_lev_percent | W | Percent / Con. | % | 2 bytes long signé |  | 0.005 | POINT 05 | DEM_LIM | GENUNIT | 激活需求限制值
nviHeatSept | SNVT_temp_p | W | Temp. / Cons | °C | 2 bytes long signé |  | 0.01 | POINT 06 | hsp1 | SETPOINT | 制热设定值1
nvoActualCapacity | SNVT_lev_percent | R | Percent | % | 2 bytes long signé |  | 0.005 | POINT 07 | CAP_T | GENUNIT | 机组总容量
nvoCapacityLim | SNVT_lev_percent | R | Percent | % | 2 bytes long signé |  | 0.005 | POINT 08 | DEM_LIM | GENUNIT | 激活需求限制值
nvoLvgCHWTemp | SNVT_temp_p | R | Temperature | °C | 2 bytes long signé |  | 0.01 | POINT 09 | LWT | TEMP | 冷水出水温
nvoEntCHWTemp | SNVT_temp_p | R | Temperature | °C | 2 bytes long signé |  | 0.01 | POINT 10 | EWT | TEMP | 冷水进水温
nvoEntCNDWTemp | SNVT_temp_p | R | Temperature | °C |  |  | 0.01 | POINT 11 | OAT | TEMP | 室外环境温度
nvoLvgCNDWTemp | SNVT_temp_p | R | Temperature | °C |  |  | 0.01 | POINT 12 | CHWSTEMP | TEMP | 冷水系统温度
nvoChillerStat.run_mode | SNVT_chlr_Status | R | N/A |  |  |  |  | POINT 13
nvoChillerStat.op_mode | SNVT_chlr_Status | R | N/A |  |  |  |  | POINT 14
nvoChillerStat.in_alarm | SNVT_chlr_Status | R | N/A |  |  |  |  | POINT 15
nvoChillerStat.run_enabl | SNVT_chlr_Status | R | N/A |  |  |  |  | POINT 16
nvoChillerStat.Local | SNVT_chlr_Status | R | N/A |  |  |  |  | POINT 17
nvoChillerStat.Limited | SNVT_chlr_Status | R | N/A |  |  |  |  | POINT 18
nvoChillerStat.chw_flow | SNVT_chlr_Status | R | N/A |  |  |  |  | POINT 19
nvoChillerStat.cndw_flow | SNVT_chlr_Status | R | N/A |  |  |  |  | POINT 20
nviOccSchedule | SNVT_tod_event | W | N/A |  |  |  |  | POINT 21
nviTEMP1 | SNVT_temp_p | W | Temp. / Cons | °C | 2 bytes long signé |  | 0.01 | POINT 22 | csp1 | SETPOINT | 制冷设定值1
nvoTEMP1 | SNVT_temp_p | R | Temperature | °C | 2 bytes long signé |  | 0.01 | POINT 23 | csp1 | SETPOINT | 制冷设定值1
nvoTEMP2 | SNVT_temp_p | R | Temperature | °C | 2 bytes long signé |  | 0.01 | POINT 24 | hsp1 | SETPOINT | 制热设定值1
nvoTEMP3 | SNVT_temp_p | R | Temperature | °C | 2 bytes long signé |  | 0.01 | POINT 25 | SCT_A | TEMP | A回饱和冷凝温度
nvoTEMP4 | SNVT_temp_p | R | Temperature | °C | 2 bytes long signé |  | 0.01 | POINT 26 | SST_A | TEMP | A回饱和吸气温度
nvoTEMP5 | SNVT_temp_p | R | Temperature | °C | 2 bytes long signé |  | 0.01 | POINT 27 | SCT_B | TEMP | A回饱和冷凝温度
nvoTEMP6 | SNVT_temp_p | R | Temperature | °C | 2 bytes long signé |  | 0.01 | POINT 28 | SST_B | TEMP | B回饱和吸气温度
nviPRESS1 | SNVT_press | W | Pressure / Con. | kPa | 2 bytes long signé |  | 0.1 | POINT 29
nvoPRESS1 | SNVT_press | R | Pressure | kPa | 2 bytes long signé |  | 0.1 | POINT 30 | DP_A | PRESSURE | A回路排气压力
nvoPRESS2 | SNVT_press | R | Pressure | kPa | 2 bytes long signé |  | 0.1 | POINT 31 | SP_A | PRESSURE | A主要吸气压力
nvoPRESS3 | SNVT_press | R | Pressure | kPa | 2 bytes long signé |  | 0.1 | POINT 32 | DP_B | PRESSURE | B回路排气压力
nvoPRESS4 | SNVT_press | R | Pressure | kPa | 2 bytes long signé |  | 0.1 | POINT 33 | SP_B | PRESSURE | B主要吸气压力
nvoPCT1 | SNVT_lev_percent | R | Percent | % | 2 bytes long signé |  | 0.005 | POINT 34
nvoPCT2 | SNVT_lev_percent | R | Percent | % | 2 bytes long signé |  | 0.005 | POINT 35
nvoTEMPDIFF1 | SNVT_temp_diff_p | R | N/A |  |  |  |  | POINT 36
nvoTEMPDIFF2 | SNVT_temp_diff_p | R | N/A |  |  |  |  | POINT 37
nviDISCRETE1 | SNVT_switch | W | Switch (*) |  | 2 bytes |  |  | POINT 38 | EMSTOP | GENUNIT | 紧急停止
nviDISCRETE2 | SNVT_switch | W | Switch (*) |  | 2 bytes |  |  | POINT 39
nvoDISCRETE1 | SNVT_switch | R | Switch (*) |  | 2 bytes |  |  | POINT 40 | EMSTOP | GENUNIT | 紧急停止
nvoDISCRETE2 | SNVT_switch | R | Switch (*) |  | 2 bytes |  |  | POINT 41 | CHIL_OCC | GENUNIT | 占用指令
nvoDISCRETE3 | SNVT_switch | R | Switch (*) |  | 2 bytes |  |  | POINT 42 | FLOW_SW | INPUTS | 流量开关状态
nvoDISCRETE4 | SNVT_switch | R | Switch (*) |  | 2 bytes |  |  | POINT 43
nvoDISCRETE5 | SNVT_switch | R | Switch (*) |  | 2 bytes |  |  | POINT 44
nvoDISCRETE6 | SNVT_switch | R | Switch (*) |  | 2 bytes |  |  | POINT 45
nviCOUNT1 | SNVT_count | W | event counter |  | 2 bytes long pas signé |  | 1 | POINT 46
nvoCOUNT1 | SNVT_count | R | event counter |  | 2 bytes long pas signé |  | 1 | POINT 47 | ALM | ALARMRST | 报警状态
nvoCOUNT2 | SNVT_count | R | event counter |  | 2 bytes long pas signé |  | 1 | POINT 48 | CTRL_TYP | GENUNIT | 本地=0 网络=1 远程=2
nvoCOUNTinc1 | SNVT_count_inc | R | event counter |  | 2 bytes long pas signé |  | 1 | POINT 49
nvoCOUNTinc2 | SNVT_count_inc | R | event counter |  | 2 bytes long pas signé |  | 1 | POINT 50