## DONNEES
SIMULATION PPT |  |  |  | Longueur | Largeur | Hauteur | Pompe HP | 1100 | 4
Matériel : 2 AQUACIATPOWER 1100 AVEC MODULE H |  |  |  | 3603 | 2253 | 2324 |  | 1200 | 5.5
effet R32
Installation Base |  | Simulation 3
AQUACIATPOWER | LD HE1100 | LD ST 1200R | Evolution vs Base
Hydr. Mod. Pompe double HP | 116S | 116W
Pompe Vitesse variable | non | Oui
Haute eff. Saisonnière | Oui | Oui
Regime 12/7°C Air 35°C
Refrigerant / GWP : | R410A / 2088 | R-32 / 675
kg | 34 | 30 | -11.76%
kg / tCO2Equ | 70.992 | 20.25 | -71.48%
Puissance frigorifique : kW | 300 | 311 | 3.667%
Efficacité froid (E.E.R.) : kW/Kw | 2.96 | 3.13 | 5.743%
Efficacité saisonnière (SEER) : kW/kW | 4.75 | 5.26 | 10.74%
effet VSD PUMP
|  | Simulation 3 |  | 2410 Longueur
| LD ST 1100 | LD ST 1100R | Evolution vs Base
| R410A / 2088 | R-32 / 675
#DIV/0!
| 0 | 0 | #DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!

## COUT
| R410A | R410A
| LD ST 1100 | LD HE 1100 | LD 1200R | LD 1200R
Options | 15LS | 15LS | 15LS | 15LS
| 28 | 28 | 28 | 28
| 116S | 116W | 116S | 116W
|  |  | 119A | 119A
TP CIAT France € | 29170 | 31500 | 31136 | 32396
Cost € | 19032 |  | 21609 | 22425
Prix vente installateur € | 33528.7356 | 36206.8966 | 35788.5057 | 37236.7816 | 13 | Marge CIAT France
Prix vente client final installé € | 41910.9195 | 45258.6207 | 44735.6322 | 46545.977 | 20 | Marge Installateur
Pour simul | 42000 | 45000 | 45000 | 47500
|  |  |  | 1.0556 | Vs FS pump
|  |  |  | 1.0556 | Vs R410A VS pump
SAME € / KW

## ENERGY COST
| LD HE 1100 | LD HE 1100 | LD 1200R | LD 1200R
Options | 15LS | 15LS | 15LS | 15LS
| 28 | 28 | 28 | 28
| 116S | 116W | 116S | 116W
|  |  | 119A | 119A
Energy Cost €/Kw. | 0.07
Nb heure fonctionnement annuel h | 3000
Nb heure fonctionnement POMPE h | 5000
Puissance pompe | 5.5 | 5.5 | 5.5 | 5.5
| R-410A Hte Efficacité Pompe Fixe | R-410A Hte Efficacité Pompe Variable | R-32 Hte Efficacité Pompe Fixe | R-32 Hte Efficacité Pompe Variable
| R-410A High Efficiency Fixed Speed Pump | R-410A High Efficiency Variable Spped Pump | R-32 High Efficiency Fixed speed Pump | R-32 High Efficiency Variable Speed Pump
Coût énergétique appareil € | 2900 | 2900 | 2700 | 2700
Coût Energétique pompe € | 1700 | 600 | 1700 | 600
Coût Energétique Annuel € | 4600 | 3500 | 4400 | 3300
Gain R32 | [5 empty] | Previous AquaSnap® 30RBM R410A | Previous AquaSnap Greenspeed® 30RBP R410A | New AquaSnap® 30RB R-32A | New AquaSnap Greenspeed® 30RBP R-32A
Gain Hte efficacité |  |  | 6.897% | 6.897% | € | 4600 | 3500 | 4400 | 3300
Gain Pompe Vitesse Variable |  | 64.71% |  | 64.71% | kWh | 65714.2857 | 50000 | 62857.1429 | 47142.8571
Gain global |  |  |  | 28.26% |  |  |  | -2857.1429 | -15714.2857
Note on A14: Pollet Eric (0033688653627): Benchvac
Note on A15: Pollet Eric (0033688653627): Benchvac

## PAY BACK
|  | R-410A Hte Efficacité Pompe Fixe | R-410A Hte Efficacité Pompe Variable | R-32 Hte Efficacité Pompe Fixe | R-32 Hte Efficacité Pompe Variable
|  | R-410A High Efficiency Fixed Speed Pump | R-410A High Efficiency Variable Spped Pump | R-32 High Efficiency Fixed speed Pump | R-32 High Efficiency Variable Speed Pump
| Coût Appareil € | 42000 | 45000 | 45000 | 47500 | 1.0556
| Coût Energétique Annuel € | 4600 | 3500 | 4400 | 3300
| Cout Maintenance Annuelle | 2200 | 2200 | 2200 | 2200
| Cout Réparation Annuelle | 1800 | 1800 | 1000 | 1000
CEE
Year 0 | Année 0 | 48800 | 50700 | 51600 | 53000 | 1.0454
Year 1 | Année 1 | 57400 | 58200 | 59200 | 59500 | 1.0223
Year 2 | Année 2 | 66000 | 65700 | 66800 | 66000 | 1.0046
Year 3 | Année 3 | 74600 | 73200 | 74400 | 72500 | 0.99044
Year 4 | Année 4 | 83200 | 80700 | 82000 | 79000 | 0.97893
Year 5 | Année 5 | 91800 | 88200 | 89600 | 85500 | 0.96939
Year 6 | Année 6 | 100400 | 95700 | 97200 | 92000 | 0.96134
Year 7 | Année 7 | 109000 | 103200 | 104800 | 98500 | 0.95446
Year 8 | Année 8 | 117600 | 110700 | 112400 | 105000 | 0.94851
Year 9 | Année 9 | 126200 | 118200 | 120000 | 111500 | 0.94332
Year 10 | Année 10 | 134800 | 125700 | 127600 | 118000 | 0.93874
Year 11 | Année 11 | 143400 | 133200 | 135200 | 124500 | 0.93468
Year 12 | Année 12 | 152000 | 140700 | 142800 | 131000 | 0.93106
Year 13 | Année 13 | 160600 | 148200 | 150400 | 137500 | 0.9278
Year 14 | Année 14 | 169200 | 155700 | 158000 | 144000 | 0.92486
Year 15 | Année 15 | 177800 | 163200 | 165600 | 150500 | 0.92218
Note on B9: Costs = (Equipment + Extra equipment + Total Annual Energy costs) - White Certificates(CEE)
Note on B10: Costs = Costs Year 0 + Total Annual Energy costs + Annual maintenance costs
Note on B11: Costs = Costs Year 1 + Total Annual Energy costs + Annual maintenance costs
Note on B12: Costs = Costs Year 2 + Total Annual Energy costs + Annual maintenance costs + Annual repair costs
Note on B13: Same calculation than Year 3 until Year 15