## Base Chiller
Description | Type de SNVT | Read/Write | Type | Unité | Format | Value | Précision | Point | 30XA/XB | 30XW | Tables | Remarks
nviChillerEnable | SNVT_switch | W | Switch (*) |  | 2 bytes | 0 /1 et 0/100% |  | POINT 01 | CHIL_S_S |  | GENUNIT : CCN Chiller Start/Stop
nviCoolSetpt | SNVT_temp_p | W | Temp. / Cons | °C | 2 bytes long signé | -273 / +327 | 0.01 | POINT 02 | CTRL_PNT |  | GENUNIT : Control Point
nvoOnOff | SNVT_switch | R | Switch (*) |  | 2 bytes | 0 /1 et 0/100% |  | POINT 03 | CHIL_S_S |  | GENUNIT : CCN Chiller Start/Stop
nvoActiveSetpt | SNVT_temp_p | R | Temperature | °C | 2 bytes long signé | -273 / +327 | 0.01 | POINT 04 | sp |  | GENUNIT : Current Setpoint
nviCapacityLim | SNVT_lev_percent | W | Percent / Con. | % | 2 bytes long signé | -163.84 / +163.83 | 0.005 | POINT 05 | DEM_LIM |  | GENUNIT : Active Demand Limit Val
nviHeatSept | SNVT_temp_p | W | Temp. / Cons | °C | 2 bytes long signé | -273 / +327 | 0.01 | POINT 06 | hsp1 |  | SETPOINT : Heating Setpoint 1
nvoActualCapacity | SNVT_lev_percent | R | Percent | % | 2 bytes long signé | -163.84 / +163.83 | 0.005 | POINT 07 | CAP_T |  | GENUNIT : Percent Total Capacity
nvoCapacityLim | SNVT_lev_percent | R | Percent | % | 2 bytes long signé | -163.84 / +163.83 | 0.005 | POINT 08 | DEM_LIM |  | GENUNIT : Active Demand Limit Val
nvoLvgCHWTemp | SNVT_temp_p | R | Temperature | °C | 2 bytes long signé | -273 / +327 | 0.01 | POINT 09 | COOL_LWT |  | TEMP : Cooler Leaving Water Temp
nvoEntCHWTemp | SNVT_temp_p | R | Temperature | °C | 2 bytes long signé | -273 / +327 | 0.01 | POINT 10 | COOL_EWT |  | TEMP : Cooler Entering Water Temp
nvoEntCNDWTemp | SNVT_temp_p | R | Temperature | °C |  | -273 / +327 | 0.01 | POINT 11 | OAT | COND_EWT | 30XB: TEMP: Outside Air Temperature 30XW: TEMP : Condenser Leaving Water Temp
nvoLvgCNDWTemp | SNVT_temp_p | R | Temperature | °C |  | -273 / +327 | 0.01 | POINT 12 | CHWSTEMP | COND_LWT | 30XB: TEMP: Master/Salve Temperature 30XW: TEMP : Condenser Entering Water Temp
nvoChillerStat.run_mode | SNVT_chlr_Status | R | Not Available |  |  |  |  | POINT 13
nvoChillerStat.op_mode | SNVT_chlr_Status | R | Not Available |  |  |  |  | POINT 14
nvoChillerStat.in_alarm | SNVT_chlr_Status | R | Not Available |  |  |  |  | POINT 15
nvoChillerStat.run_enabl | SNVT_chlr_Status | R | Not Available |  |  |  |  | POINT 16
nvoChillerStat.Local | SNVT_chlr_Status | R | Not Available |  |  |  |  | POINT 17
nvoChillerStat.Limited | SNVT_chlr_Status | R | Not Available |  |  |  |  | POINT 18
nvoChillerStat.chw_flow | SNVT_chlr_Status | R | Not Available |  |  |  |  | POINT 19
nvoChillerStat.cndw_flow | SNVT_chlr_Status | R | Not Available |  |  |  |  | POINT 20
nviOccSchedule | SNVT_tod_event | W | Not Available |  |  |  |  | POINT 21
nviTEMP1 | SNVT_temp_p | W | Temp. / Cons | °C | 2 bytes long signé | -273 / +327 | 0.01 | POINT 22 | csp1 |  | SETPOINT : Cooling Setpoint 1
nvoTEMP1 | SNVT_temp_p | R | Temperature | °C | 2 bytes long signé | -273 / +327 | 0.01 | POINT 23 | csp1 |  | SETPOINT : Cooling Setpoint 1
nvoTEMP2 | SNVT_temp_p | R | Temperature | °C | 2 bytes long signé | -273 / +327 | 0.01 | POINT 24 | hsp1 |  | SETPOINT : Heating Setpoint 1
nvoTEMP3 | SNVT_temp_p | R | Temperature | °C | 2 bytes long signé | -273 / +327 | 0.01 | POINT 25 | SCT_A |  | TEMP : Saturated Condensing Temp circuit A
nvoTEMP4 | SNVT_temp_p | R | Temperature | °C | 2 bytes long signé | -273 / +327 | 0.01 | POINT 26 | SST_A |  | TEMP : Saturated Suction Temp circuit A
nvoTEMP5 | SNVT_temp_p | R | Temperature | °C | 2 bytes long signé | -273 / +327 | 0.01 | POINT 27 | SCT_B |  | TEMP : Saturated Condensing Temp circuit B
nvoTEMP6 | SNVT_temp_p | R | Temperature | °C | 2 bytes long signé | -273 / +327 | 0.01 | POINT 28 | SST_B |  | TEMP : Saturated Suction Temp circuit B
nviPRESS1 | SNVT_press | W | Pressure / Con. | kPa | 2 bytes long signé | -3276 / +3276 | 0.1 | POINT 29
nvoPRESS1 | SNVT_press | R | Pressure | kPa | 2 bytes long signé | -3276 / +3276 | 0.1 | POINT 30 | DP_A |  | PRESSURE : Discharge Pressure circuit A
nvoPRESS2 | SNVT_press | R | Pressure | kPa | 2 bytes long signé | -3276 / +3276 | 0.1 | POINT 31 | SP_A |  | PRESSURE : Suction Pressure circuit A
nvoPRESS3 | SNVT_press | R | Pressure | kPa | 2 bytes long signé | -3276 / +3276 | 0.1 | POINT 32 | DP_B |  | PRESSURE : Discharge Pressure circuit B
nvoPRESS4 | SNVT_press | R | Pressure | kPa | 2 bytes long signé | -3276 / +3276 | 0.1 | POINT 33 | SP_B |  | PRESSURE : Suction Pressure circuit B
nvoPCT1 | SNVT_lev_percent | W | Percent | % | 2 bytes long signé | -163.84 / +163.83 | 0.005 | POINT 34
nvoPCT2 | SNVT_lev_percent | W | Percent | % | 2 bytes long signé | -163.84 / +163.83 | 0.005 | POINT 35
nvoTEMPDIFF1 | SNVT_temp_diff_p | R | Not Available |  |  |  |  | POINT 36
nvoTEMPDIFF2 | SNVT_temp_diff_p | R | Not Available |  |  |  |  | POINT 37
nviDISCRETE1 | SNVT_switch | W | Switch (*) |  | 2 bytes | 0 /1 et 0/100% |  | POINT 38 | EMSTOP |  | GENUNIT : Emergency Stop
nviDISCRETE2 | SNVT_switch | W | Switch (*) |  | 2 bytes | 0 /1 et 0/100% |  | POINT 39
nvoDISCRETE1 | SNVT_switch | R | Switch (*) |  | 2 bytes | 0 /1 et 0/100% |  | POINT 40 | EMSTOP |  | GENUNIT : Emergency Stop
nvoDISCRETE2 | SNVT_switch | R | Switch (*) |  | 2 bytes | 0 /1 et 0/100% |  | POINT 41 | CHIL_OCC |  | GENUNIT : Chiller Occupied?
nvoDISCRETE3 | SNVT_switch | R | Switch (*) |  | 2 bytes | 0 /1 et 0/100% |  | POINT 42 | FLOW_SW |  | PUMPSTAT : Cooler Flow Switch
nvoDISCRETE4 | SNVT_switch | R | Switch (*) |  | 2 bytes | 0 /1 et 0/100% |  | POINT 43
nvoDISCRETE5 | SNVT_switch | R | Switch (*) |  | 2 bytes | 0 /1 et 0/100% |  | POINT 44
nvoDISCRETE6 | SNVT_switch | R | Switch (*) |  | 2 bytes | 0 /1 et 0/100% |  | POINT 45
nviCOUNT1 | SNVT_count | W | event counter |  | 2 bytes long pas signé | 0 / 65535 | 1 | POINT 46
nvoCOUNT1 | SNVT_count | R | event counter |  | 2 bytes long pas signé | 0 / 65535 | 1 | POINT 47 | ALM |  | ALARMRST : Normal=0 Partial=1 Shutdown=2
nvoCOUNT2 | SNVT_count | R | event counter |  | 2 bytes long pas signé | 0 / 65535 | 1 | POINT 48 | CTRL_TYP |  | GENUNIT : Local=0 Net.=1 Remote=2
nvoCOUNTinc1 | SNVT_count_inc | R | event counter |  | 2 bytes long pas signé | -32768 / 32767 | 1 | POINT 49
nvoCOUNTinc2 | SNVT_count_inc | R | event counter |  | 2 bytes long pas signé | -32768 / 32767 | 1 | POINT 50